## Summary
Circuit | Substation | 2019 Wildfire Risk Group1 | 2020 Wildfire Risk Group1 | 2021 Wildfire Risk Group1 | 2022 Wildfire Risk Group1 | 2023 Wildfire Risk Group2 | 2024 Wildfire Risk Group2 | 2025 Wildfire Risk Group2 | 2033 Wildfire Risk Group2
Radford | SCE Feed | 30520.52 | 30620.52 | 31214.88 | 31214.88 | 522 | 522 | 522 | 522
Shay | SCE Feed | 14230.0367 | 13366.5167 | 7102.5967 | 3524.4967 | 0 | 0 | 0 | 0
Baldwin | SCE Feed | 7185.34 | 7762.81 | 7606.01 | 6890.98 | 6890.98 | 3197.28 | 345.4 | 345.4
Boulder | Village | 3350.98 | 2950.98 | 1229.62 | 882.12 | 882.12 | 882.12 | 0 | 0
North Shore (Fawnskin) | Fawnskin | 7518.0467 | 7538.0467 | 6721.2367 | 6717.2367 | 6717.2367 | 6094.5367 | 4585.2367 | 0
Erwin Lake | Maltby | 7401.2729 | 3415.6729 | 2005.5429 | 0 | 0 | 0 | 0 | 0
Pioneer (Palomino) | Palomino | 5706.29 | 5206.29 | 2425.88 | 2729.88 | 2729.88 | 2729.88 | 2729.88 | 0
Clubview | Moonridge | 3459.98 | 4059.98 | 3330.72 | 3225.04 | 3010.92 | 2202.92 | 1192.92 | 0
Goldmine | Moonridge | 5559.2 | 6659.2 | 4490.8 | 4538.8 | 4538.8 | 3730.8 | 2720.8 | 0
Paradise | Maltby | 3493.0167 | 3493.0167 | 2894.4467 | 1809.5467 | 1242.4667 | 1242.4667 | 1242.4667 | 0
Sunset | Maple | 3583.37 | 3883.37 | 2533.02 | 2373.52 | 2074.56 | 2074.56 | 258.56 | 0
Sunrise (Maple) | Maple | 2649.69 | 2649.69 | 2216.89 | 1856.69 | 1711.93 | 1711.93 | 395.93 | 0
Holcomb (Bear City) | Bear City | 5915.75 | 4515.75 | 4205 | 4746.15 | 4746.15 | 3412.95 | 2604.95 | 1382.15
Georgia | Pineknot | 1918.81 | 2018.81 | 1280.19 | 1384.19 | 1103 | 1103 | 1103 | 847
Eagle | Pineknot | 2072.3467 | 2072.3467 | 1812.6867 | 1812.6867 | 1508.5167 | 1508.5167 | 1508.5167 | 521.5167
Harnish (Village) | Village | 385.44 | 585.44 | 792.76 | 786.06 | 786.06 | 786.06 | 786.06 | 742.06
Garstin | Meadow | 2439.81 | 1749.94 | 1391.76 | 1366.31 | 905.51 | 905.51 | 905.51 | 845.51
Lagonita | Village | 2023.36 | 2323.36 | 1576.44 | 1533.14 | 1453.14 | 1453.14 | 1453.14 | 374.14
Interlaken | Meadow | 3274.95 | 2474.95 | 1652.3 | 1485.16 | 1116.68 | 1116.68 | 1116.68 | 1008.68
Castle Glen (Division) | Division | 1982.48 | 2238.39 | 2364.91 | 1483.32 | 1483.32 | 1483.32 | 1303.32 | 495.32
Country Club | Division | 983.6467 | 845.1467 | 708.7867 | 639.5367 | 639.5367 | 639.5367 | 639.5367 | 607.5367
Fox Farm | Meadow | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump House (Lake) | Lake | 287.04 | 287.04 | 201.76 | 201.76 | 201.76 | 201.76 | 201.76 | 201.76
Lift (Summit TOU) | Summit | 27.6 | 27.6 | 627.4 | 627.4 | 626.9 | 626.9 | 626.9 | 626.9
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 115968.9762 | 110744.8662 | 90385.6362 | 81828.9033 | 44891.4667 | 37625.8667 | 26242.5667 | 8519.9733
1Actual risk values at end of year (December 31) based on actual WMP initiatives accomplished
2Estimated risk values based on planned WMP initiatives at end of year (December 31)
Wildfire Risk Groups
|  | High | >3000
|  | Moderate | 1201-2999
|  | Low | <1200

## Circuit Status 2033 Estimate
Circuit Information | [22 empty] | Wildfire T&D Hardening | [9 empty] | O&M Programs Implemented
Algorithm Input = AI | [5 empty] | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI | AI | [5 empty] | AI |  | AI |  | AI | AI | AI | AI | AI | AI | AI
Circuit | Substation | Wildfire Risk Group | Wildfire Risk Group | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked) | Pole Loading Program (Percent Complete) | Tree Attachment Removal Program | Repalce OH Bare Wire with Covered Conductor | Replace Expulsion Fuses | Evacuation Route Hardening | Circuit Sectionalized to Reduce PSPS Impact | Fault Indicators | Replace AR with Pulse Conditioned Intellirupter | Circuit Meters Installed On All Phases Remotely Monitored | Install FLISR | Enhanced Vegetation Management | GO-165 Ground Patrol | GO-165 5-Year Inspections | GO-165 Intrussive Inspections | Annual LiDAR Survey | 3rd Party Annual Ground Patrol | GO-174 Substation Inspections | Substation Electrical Equipment Preventative Maintenance | Exacter Survey | Fly-over Video Inspection Survey | Evaluate Protective Settings & Optimize for Fire Safety
Radford | SCE Feed | 522 | 522 | -0.03881 | 8 | 34.5 | 3 | High | High | 3437 | 89 | 0 | 0 | 0 | 0 | 2.82 | 0.02 | 0 | 0 | 0 | 0 | 4 | 0% | None |  | NA |  |  | NA |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Shay | SCE Feed | -1260.1333 | 0 | 0.09369 | 22 | 34.5 | 2 | Medium | High | 9582 | 586 | 0 | 24 | 0 | 0 | 17.17 | 0.39 | 0 | 0 | 0 | 0 | 1 | 36% | None |  | NA |  |  | 33.33% |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Baldwin | SCE Feed | 345.4 | 345.4 | -0.02568 | 12 | 34.5 | 2 | Medium | High | 11621 | 236 | 0 | 20 | 0 | 0 | 8.94 | 0.5 | 0 | 0 | 0 | 0 | 2 | 7% | None |  | NA |  |  | 0% |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Boulder | Village | -6335 | 0 | 0.471 | 25 | 4.16 | 2 | Medium | High | 2015 | 990 | 22 | 6 | 0 | 0 | 17.68 | 1.8 | 0 | 0 | 0 | 0 | 9 | 90% | 80.27% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
North Shore (Fawnskin) | Fawnskin | -1081.3333 | 0 | 0.080396 | 20 | 4.16 | 2 | High | High | 1512 | 924 | 0 | 0 | 0 | 0 | 15.83 | 8.09 | 0 | 0 | 0 | 0 | 3 | 0% | 79.93% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Erwin Lake | Maltby | -6512.2571 | 0 | 0.48418 | 26 | 4.16 | 2 | Medium | High | 2574 | 1054 | 2 | 6 | 0 | 0 | 21.33 | 7.41 | 0 | 0 | 0 | 0 | NR | 82% | [5 empty] | 82.86% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pioneer (Palomino) | Palomino | -1803 | 0 | 0.13405 | 24 | 4.16 | 2 | Medium | High | 534 | 601 | 0 | 1 | 0 | 0 | 16.39 | 2.95 | 0 | 0 | 0 | 0 | NR | 20% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Clubview | Moonridge | -774 | 0 | 0.057546 | 17 | 4.16 | 2 | High | Medium | 1723 | 507 | 3 | 2 | 0 | 0 | 10.18 | 0.27 | 0 | 0 | 0 | 0 | 8 | 0% | 84.09% |  |  |  |  | 60% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Goldmine | Moonridge | -842 | 0 | 0.062602 | 19 | 4.16 | 2 | Medium | High | 2033 | 601 | 0 | 0 | 0 | 0 | 13.2 | 5.26 | 0 | 0 | 0 | 0 | 7 | 0% | [5 empty] | 40% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Paradise | Maltby | -1363.3333 | 0 | 0.10136 | 23 | 4.16 | 2 | Medium | High | 1874 | 532 | 3 | 17 | 0 | 0 | 9.85 | 2 | 0 | 0 | 0 | 0 | NR | 10% | 7.25% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunset | Maple | -1212 | 0 | 0.090111 | 21 | 4.16 | 2 | High | Medium | 1894 | 505 | 0 | 0 | 0 | 0 | 10.67 | 0.5 | 0 | 0 | 0 | 0 | NR | 8% | 5.66% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunrise (Maple) | Maple | -783 | 0 | 0.058215 | 18 | 4.16 | 2 | Medium | Medium | 1772 | 348 | 0 | 0 | 0 | 0 | 8.62 | 3.86 | 0 | 0 | 0 | 0 | NR | 5% | 5.56% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Holcomb (Bear City) | Bear City | 1382.15 | 1382.15 | -0.10276 | 1 | 4.16 | 2 | Medium | High | 1581 | 609 | 2 | 4 | 0 | 5.15 | 8.1 | 0.85 | 0 | 0 | 0 | 6 | NR | 1% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Georgia | Pineknot | 847 | 847 | -0.062974 | 3 | 4.16 | 2 | Medium | Low | 935 | 349 | 0 | 0 | 0 | 5 | 0.91 | 3.95 | 0 | 0 | 0 | 1 | NR | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Eagle | Pineknot | 521.5167 | 521.5167 | -0.038774 | 9 | 4.16 | 2 | Medium | Medium | 689 | 323 | 0 | 0 | 0 | 3.65 | 3.73 | 1.53 | 0 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Harnish (Village) | Village | 742.06 | 742.06 | -0.055171 | 5 | 4.16 | 2 | Medium | Low | 327 | 86 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 0 | 0 | 0 | 0 | 6 | 0% | 15.38% |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Garstin | Meadow | 845.51 | 845.51 | -0.062863 | 4 | 4.16 | 2 | High | Low | 1347 | 277 | 0 | 0 | 0 | 3.89 | 2.02 | 3 | 0 | 0 | 0 | 0 | NR | 5% | 0% |  |  |  |  | 25% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lagonita | Village | 374.14 | 374.14 | -0.027817 | 11 | 4.16 | 2 | Medium | Low | 1095 | 452 | 1 | 0 | 0 | 4.46 | 3 | 1.43 | 0 | 0 | 0 | 0 | NR | 0% | 3.33% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Interlaken | Meadow | 1008.68 | 1008.68 | -0.074994 | 2 | 4.16 | 2 | Medium | Medium | 889 | 280 | 0 | 0 | 0 | 4.92 | 1.53 | 3.55 | 0 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Castle Glen (Division) | Division | 495.32 | 495.32 | -0.036827 | 10 | 4.16 | 2 | Medium | High | 1216 | 340 | 9 | 2 | 0 | 3.33 | 2.6 | 3.68 | 0 | 0 | 0 | 0 | 10 | 10% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Country Club | Division | 607.5367 | 607.5367 | -0.04517 | 7 | 4.16 | 2 | Medium | Medium | 596 | 178 | 1 | 0 | 0 | 3.03 | 0.15 | 0.94 | 0 | 0 | 0 | 0 | NR | 0% | 20% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Fox Farm | Meadow | -4 | 0 | 0.0002974 | 16 | 4.16 | 2 | Low | Low | 28 | 2 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pump House (Lake) | Lake | 201.76 | 201.76 | -0.015001 | 13 | 4.16 | 2 | Low | High | 3 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lift (Summit TOU) | Summit | 626.9 | 626.9 | -0.046609 | 6 | 4.16 | 2 | Low | Low | 0 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 14 | 4.16 | 2 | Low | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 14 | 4.16 | 2 | Low | Low | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
|  | -13450.0838 | 8519.9733 | 1 | [6 empty] | 9892 | 43 | 82 | 0 | 35.51 | 174.72 | 54.08 | 0 | 0 | 0 | 7
|  |  | Wildfire Risk Groups | [19 empty] | Status
|  |  | High | [20 empty] | Not Started
|  |  | Moderate | [20 empty] | In Progress
|  |  | Low | [20 empty] | Complete or Implemented
Not Applicable
[15 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[15 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[14 empty] | 34 kV | 0 | 28.93 | 0.91 | 29.84
[14 empty] | 4 kV | 35.51 | 145.79 | 53.17 | 234.47
[14 empty] | Total | 35.51 | 174.72 | 54.08 | 264.31
[15 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[14 empty] | 34 kV | 0% | 10.95% | 0.3443% | 11.29%
[14 empty] | 4 kV | 13.43% | 55.16% | 20.12% | 88.71%
[14 empty] | Total | 13.43% | 66.1% | 20.46% | 100%
[15 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[14 empty] | 34 kV | 0% | 96.95% | 3.05%
[15 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[14 empty] | 4 kV | 15.14% | 62.18% | 22.68%

## Circuit Status 2025 Estimate
Circuit Information | [22 empty] | Wildfire T&D Hardening | [9 empty] | O&M Programs Implemented
Algorithm Input = AI | [5 empty] | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI | AI | [5 empty] | AI |  | AI |  | AI | AI | AI | AI | AI | AI | AI
Circuit | Substation | Wildfire Risk Group | Wildfire Risk Group | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked) | Pole Loading Program (Percent Complete) | Tree Attachment Removal Program | Repalce OH Bare Wire with Covered Conductor | Replace Expulsion Fuses | Evacuation Route Hardening | Circuit Sectionalized to Reduce PSPS Impact | Fault Indicators | Replace AR with Pulse Conditioned Intellirupter | Circuit Meters Installed On All Phases Remotely Monitored | Install FLISR | Enhanced Vegetation Management | GO-165 Ground Patrol | GO-165 5-Year Inspections | GO-165 Intrussive Inspections | Annual LiDAR Survey | 3rd Party Annual Ground Patrol | GO-174 Substation Inspections | Substation Electrical Equipment Preventative Maintenance | Exacter Survey | Fly-over Video Inspection Survey | Evaluate Protective Settings & Optimize for Fire Safety
Radford | SCE Feed | 522 | 522 | 0.02256 | 16 | 34.5 | 3 | High | High | 3437 | 89 | 0 | 0 | 0 | 0 | 2.82 | 0.02 | 0 | 0 | 0 | 0 | 4 | 0% | None |  | NA |  |  | NA |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Shay | SCE Feed | -1011.0233 | 0 | -0.043694 | 25 | 34.5 | 2 | Medium | High | 9582 | 586 | 0 | 24 | 0 | 0.29 | 16.88 | 0.39 | 0 | 0 | 0 | 0 | 1 | 36% | None |  | NA |  |  | 33.33% |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Baldwin | SCE Feed | 345.4 | 345.4 | 0.014927 | 18 | 34.5 | 2 | Medium | High | 11621 | 236 | 0 | 20 | 0 | 0 | 8.94 | 0.5 | 0 | 0 | 0 | 0 | 2 | 7% | None |  | NA |  |  | 0% |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Boulder | Village | -969.88 | 0 | -0.041916 | 24 | 4.16 | 2 | Medium | High | 2015 | 990 | 22 | 6 | 0 | 13.28 | 4.4 | 1.8 | 0 | 0 | 0 | 0 | 9 | 90% | 80.27% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
North Shore (Fawnskin) | Fawnskin | 4585.2367 | 4585.2367 | 0.19816 | 1 | 4.16 | 2 | High | High | 1512 | 924 | 0 | 0 | 0 | 11.83 | 4 | 8.09 | 0 | 0 | 0 | 0 | 3 | 0% | 79.93% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Erwin Lake | Maltby | -1118.8971 | 0 | -0.048356 | 26 | 4.16 | 2 | Medium | High | 2574 | 1054 | 2 | 6 | 0 | 13.34 | 7.99 | 7.41 | 1 | 0 | 0 | 0 | NR | 82% | [5 empty] | 82.86% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pioneer (Palomino) | Palomino | 2729.88 | 2729.88 | 0.11798 | 2 | 4.16 | 2 | Medium | High | 534 | 601 | 0 | 1 | 0 | 11.22 | 5.17 | 2.95 | 0 | 0 | 0 | 0 | NR | 20% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Clubview | Moonridge | 1192.92 | 1192.92 | 0.051555 | 9 | 4.16 | 2 | High | Medium | 1723 | 507 | 3 | 2 | 0 | 4.73 | 5.45 | 0.27 | 14 | 0 | 0 | 0 | 8 | 0% | 84.09% |  |  |  |  | 60% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Goldmine | Moonridge | 2720.8 | 2720.8 | 0.11759 | 3 | 4.16 | 2 | Medium | High | 2033 | 601 | 0 | 0 | 0 | 8.7 | 4.5 | 5.26 | 12 | 0 | 0 | 0 | 7 | 0% | [5 empty] | 40% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Paradise | Maltby | 1242.4667 | 1242.4667 | 0.053696 | 8 | 4.16 | 2 | Medium | High | 1874 | 532 | 3 | 17 | 0 | 6.45 | 3.4 | 2 | 0 | 0 | 0 | 0 | NR | 10% | 7.25% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunset | Maple | 258.56 | 258.56 | 0.011174 | 19 | 4.16 | 2 | High | Medium | 1894 | 505 | 0 | 0 | 0 | 3.64 | 7.03 | 0.5 | 0 | 0 | 0 | 0 | NR | 8% | 5.66% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunrise (Maple) | Maple | 395.93 | 395.93 | 0.017111 | 17 | 4.16 | 2 | Medium | Medium | 1772 | 348 | 0 | 0 | 0 | 3.17 | 4.62 | 3.86 | 34 | 0 | 0 | 0 | NR | 5% | 5.56% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Holcomb (Bear City) | Bear City | 2604.95 | 2604.95 | 0.11258 | 4 | 4.16 | 2 | Medium | High | 1581 | 609 | 2 | 4 | 0 | 7.85 | 5.4 | 0.85 | 33 | 0 | 0 | 6 | NR | 1% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Georgia | Pineknot | 1103 | 1103 | 0.047669 | 11 | 4.16 | 2 | Medium | Low | 935 | 349 | 0 | 0 | 0 | 5 | 0.91 | 3.95 | 64 | 0 | 0 | 1 | NR | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Eagle | Pineknot | 1508.5167 | 1508.5167 | 0.065194 | 5 | 4.16 | 2 | Medium | Medium | 689 | 323 | 0 | 0 | 0 | 6.65 | 0.73 | 1.53 | 0 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Harnish (Village) | Village | 786.06 | 786.06 | 0.033972 | 13 | 4.16 | 2 | Medium | Low | 327 | 86 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 11 | 0 | 0 | 0 | 6 | 0% | 15.38% |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Garstin | Meadow | 905.51 | 905.51 | 0.039134 | 12 | 4.16 | 2 | High | Low | 1347 | 277 | 0 | 0 | 0 | 3.89 | 2.02 | 3 | 15 | 0 | 0 | 0 | NR | 5% | 0% |  |  |  |  | 25% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lagonita | Village | 1453.14 | 1453.14 | 0.062801 | 6 | 4.16 | 2 | Medium | Low | 1095 | 452 | 1 | 0 | 0 | 7.46 | 0 | 1.43 | 38 | 0 | 0 | 0 | NR | 0% | 3.33% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Interlaken | Meadow | 1116.68 | 1116.68 | 0.04826 | 10 | 4.16 | 2 | Medium | Medium | 889 | 280 | 0 | 0 | 0 | 4.92 | 1.53 | 3.55 | 27 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Castle Glen (Division) | Division | 1303.32 | 1303.32 | 0.056326 | 7 | 4.16 | 2 | Medium | High | 1216 | 340 | 9 | 2 | 0 | 5.33 | 1.6 | 3.68 | 0 | 0 | 0 | 0 | 10 | 10% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Country Club | Division | 639.5367 | 639.5367 | 0.027639 | 14 | 4.16 | 2 | Medium | Medium | 596 | 178 | 1 | 0 | 0 | 3.03 | 0.15 | 0.94 | 8 | 0 | 0 | 0 | NR | 0% | 20% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Fox Farm | Meadow | -4 | 0 | -0.00017287 | 23 | 4.16 | 2 | Low | Low | 28 | 2 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pump House (Lake) | Lake | 201.76 | 201.76 | 0.0087196 | 20 | 4.16 | 2 | Low | High | 3 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lift (Summit TOU) | Summit | 626.9 | 626.9 | 0.027093 | 15 | 4.16 | 2 | Low | Low | 0 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 21 | 4.16 | 2 | Low | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 21 | 4.16 | 2 | Low | Low | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
|  | 23138.7662 | 26242.5667 | 1 | [6 empty] | 9892 | 43 | 82 | 0 | 122.86 | 87.54 | 54.08 | 257 | 0 | 0 | 7
|  |  | Wildfire Risk Groups | [19 empty] | Status
|  |  | High | [20 empty] | Not Started
|  |  | Moderate | [20 empty] | In Progress
|  |  | Low | [20 empty] | Complete or Implemented
Not Applicable
[15 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[15 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[14 empty] | 34 kV | 0.29 | 28.64 | 0.91 | 29.84
[14 empty] | 4 kV | 122.57 | 58.9 | 53.17 | 234.64
[14 empty] | Total | 122.86 | 87.54 | 54.08 | 264.48
[15 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[14 empty] | 34 kV | 0.1096% | 10.83% | 0.3441% | 11.28%
[14 empty] | 4 kV | 46.34% | 22.27% | 20.1% | 88.72%
[14 empty] | Total | 46.45% | 33.1% | 20.45% | 100%
[15 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[14 empty] | 34 kV | 0.9718% | 95.98% | 3.05%
[15 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[14 empty] | 4 kV | 52.24% | 25.1% | 22.66%

## Circuit Status 2024 Estimate
Circuit Information | [22 empty] | Wildfire T&D Hardening | [9 empty] | O&M Programs Implemented
Algorithm Input = AI | [5 empty] | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI | AI | [5 empty] | AI |  | AI |  | AI | AI | AI | AI | AI | AI | AI
Circuit | Substation | Wildfire Risk Group | Wildfire Risk Group | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked) | Pole Loading Program (Percent Complete) | Tree Attachment Removal Program | Repalce OH Bare Wire with Covered Conductor | Replace Expulsion Fuses | Evacuation Route Hardening | Circuit Sectionalized to Reduce PSPS Impact | Fault Indicators | Replace AR with Pulse Conditioned Intellirupter | Circuit Meters Installed On All Phases Remotely Monitored | Install FLISR | Enhanced Vegetation Management | GO-165 Ground Patrol | GO-165 5-Year Inspections | GO-165 Intrussive Inspections | Annual LiDAR Survey | 3rd Party Annual Ground Patrol | GO-174 Substation Inspections | Substation Electrical Equipment Preventative Maintenance | Exacter Survey | Fly-over Video Inspection Survey | Evaluate Protective Settings & Optimize for Fire Safety
Radford | SCE Feed | 522 | 522 | 0.014367 | 20 | 34.5 | 3 | High | High | 3437 | 89 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 4 | 0% | None |  | NA |  |  | NA |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Shay | SCE Feed | -169.2033 | 0 | -0.0046569 | 25 | 34.5 | 2 | Medium | High | 9582 | 586 | 0 | 24 | 0 | 1.27 | 15.9 | 0.39 | 0 | 0 | 0 | 0 | 1 | 36% | None |  | NA |  |  | 33.33% |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Baldwin | SCE Feed | 3197.28 | 3197.28 | 0.087997 | 4 | 34.5 | 2 | Medium | High | 11621 | 236 | 0 | 20 | 0 | 3.32 | 4.62 | 0.5 | 0 | 0 | 0 | 0 | 2 | 7% | None |  | NA |  |  | 0% |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Boulder | Village | 882.12 | 882.12 | 0.024278 | 16 | 4.16 | 2 | Medium | High | 2015 | 990 | 22 | 6 | 0 | 17.28 | 0.4 | 1.8 | 59 | 0 | 0 | 0 | 9 | 90% | 80.27% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
North Shore (Fawnskin) | Fawnskin | 6094.5367 | 6094.5367 | 0.16774 | 1 | 4.16 | 2 | High | High | 1512 | 924 | 0 | 0 | 0 | 14.53 | 1.3 | 8.09 | 54 | 0 | 0 | 0 | 3 | 0% | 79.93% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Erwin Lake | Maltby | -1118.8971 | 0 | -0.030795 | 26 | 4.16 | 2 | Medium | High | 2574 | 1054 | 2 | 6 | 0 | 13.34 | 7.99 | 7.41 | 1 | 0 | 0 | 0 | NR | 82% | [5 empty] | 82.86% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pioneer (Palomino) | Palomino | 2729.88 | 2729.88 | 0.075133 | 5 | 4.16 | 2 | Medium | High | 534 | 601 | 0 | 1 | 0 | 11.22 | 5.17 | 2.95 | 0 | 0 | 0 | 0 | NR | 20% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Clubview | Moonridge | 2202.92 | 2202.92 | 0.06063 | 6 | 4.16 | 2 | High | Medium | 1723 | 507 | 3 | 2 | 0 | 7.23 | 2.95 | 0.27 | 14 | 0 | 0 | 0 | 8 | 0% | 84.09% |  |  |  |  | 60% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Goldmine | Moonridge | 3730.8 | 3730.8 | 0.10268 | 2 | 4.16 | 2 | Medium | High | 2033 | 601 | 0 | 0 | 0 | 11.2 | 2 | 5.26 | 12 | 0 | 0 | 0 | 7 | 0% | [5 empty] | 40% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Paradise | Maltby | 1242.4667 | 1242.4667 | 0.034196 | 12 | 4.16 | 2 | Medium | High | 1874 | 532 | 3 | 17 | 0 | 6.45 | 3.4 | 2 | 0 | 0 | 0 | 0 | NR | 10% | 7.25% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunset | Maple | 2074.56 | 2074.56 | 0.057097 | 7 | 4.16 | 2 | High | Medium | 1894 | 505 | 0 | 0 | 0 | 7.64 | 3.03 | 0.5 | 50 | 0 | 0 | 0 | NR | 8% | 5.66% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunrise (Maple) | Maple | 1711.93 | 1711.93 | 0.047117 | 8 | 4.16 | 2 | Medium | Medium | 1772 | 348 | 0 | 0 | 0 | 7.17 | 0.62 | 3.86 | 34 | 0 | 0 | 0 | NR | 5% | 5.56% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Holcomb (Bear City) | Bear City | 3412.95 | 3412.95 | 0.093933 | 3 | 4.16 | 2 | Medium | High | 1581 | 609 | 2 | 4 | 0 | 9.85 | 3.4 | 0.85 | 33 | 0 | 0 | 6 | NR | 1% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Georgia | Pineknot | 1103 | 1103 | 0.030357 | 14 | 4.16 | 2 | Medium | Low | 935 | 349 | 0 | 0 | 0 | 5 | 0.91 | 3.95 | 64 | 0 | 0 | 1 | NR | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Eagle | Pineknot | 1508.5167 | 1508.5167 | 0.041518 | 9 | 4.16 | 2 | Medium | Medium | 689 | 323 | 0 | 0 | 0 | 6.65 | 0.73 | 1.53 | 0 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Harnish (Village) | Village | 786.06 | 786.06 | 0.021634 | 17 | 4.16 | 2 | Medium | Low | 327 | 86 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 11 | 0 | 0 | 0 | 6 | 0% | 15.38% |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Garstin | Meadow | 905.51 | 905.51 | 0.024922 | 15 | 4.16 | 2 | High | Low | 1347 | 277 | 0 | 0 | 0 | 3.89 | 2.02 | 3 | 15 | 0 | 0 | 0 | NR | 5% | 0% |  |  |  |  | 25% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lagonita | Village | 1453.14 | 1453.14 | 0.039994 | 11 | 4.16 | 2 | Medium | Low | 1095 | 452 | 1 | 0 | 0 | 7.46 | 0 | 1.43 | 38 | 0 | 0 | 0 | NR | 0% | 3.33% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Interlaken | Meadow | 1116.68 | 1116.68 | 0.030734 | 13 | 4.16 | 2 | Medium | Medium | 889 | 280 | 0 | 0 | 0 | 4.92 | 1.53 | 3.55 | 27 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Castle Glen (Division) | Division | 1483.32 | 1483.32 | 0.040825 | 10 | 4.16 | 2 | Medium | High | 1216 | 340 | 9 | 2 | 0 | 5.33 | 1.6 | 3.68 | 45 | 0 | 0 | 0 | 10 | 10% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Country Club | Division | 639.5367 | 639.5367 | 0.017602 | 18 | 4.16 | 2 | Medium | Medium | 596 | 178 | 1 | 0 | 0 | 3.03 | 0.15 | 0.94 | 8 | 0 | 0 | 0 | NR | 0% | 20% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Fox Farm | Meadow | -4 | 0 | -0.00011009 | 24 | 4.16 | 2 | Low | Low | 28 | 2 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pump House (Lake) | Lake | 201.76 | 201.76 | 0.005553 | 21 | 4.16 | 2 | Low | High | 3 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lift (Summit TOU) | Summit | 626.9 | 626.9 | 0.017254 | 19 | 4.16 | 2 | Low | Low | 0 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 22 | 4.16 | 2 | Low | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 22 | 4.16 | 2 | Low | Low | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
|  | 36333.7662 | 37625.8667 | 1 | [6 empty] | 9892 | 43 | 82 | 0 | 148.86 | 57.72 | 54.08 | 465 | 0 | 0 | 7
|  |  | Wildfire Risk Groups | [19 empty] | Status
|  |  | High | [20 empty] | Not Started
|  |  | Moderate | [20 empty] | In Progress
|  |  | Low | [20 empty] | Complete or Implemented
Not Applicable
[15 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[15 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[14 empty] | 34 kV | 4.59 | 20.52 | 0.91 | 26.02
[14 empty] | 4 kV | 144.27 | 37.2 | 53.17 | 234.64
[14 empty] | Total | 148.86 | 57.72 | 54.08 | 260.66
[15 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[14 empty] | 34 kV | 1.761% | 7.872% | 0.3491% | 9.982%
[14 empty] | 4 kV | 55.35% | 14.27% | 20.4% | 90.02%
[14 empty] | Total | 57.11% | 22.14% | 20.75% | 100%
[15 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[14 empty] | 34 kV | 17.64% | 78.86% | 3.497%
[15 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[14 empty] | 4 kV | 61.49% | 15.85% | 22.66%

## Circuit Status 2023 Estimate
Circuit Information | [22 empty] | Wildfire T&D Hardening | [9 empty] | O&M Programs Implemented
Algorithm Input = AI | [5 empty] | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI | AI | [5 empty] | AI |  | AI |  | AI | AI | AI | AI | AI | AI | AI
Circuit | Substation | Wildfire Risk Group | Wildfire Risk Group | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked) | Pole Loading Program (Percent Complete) | Tree Attachment Removal Program | Repalce OH Bare Wire with Covered Conductor | Replace Expulsion Fuses | Evacuation Route Hardening | Circuit Sectionalized to Reduce PSPS Impact | Fault Indicators | Replace AR with Pulse Conditioned Intellirupter | Circuit Meters Installed On All Phases Remotely Monitored | Install FLISR | Enhanced Vegetation Management | GO-165 Ground Patrol | GO-165 5-Year Inspections | GO-165 Intrussive Inspections | Annual LiDAR Survey | 3rd Party Annual Ground Patrol | GO-174 Substation Inspections | Substation Electrical Equipment Preventative Maintenance | Exacter Survey | Fly-over Video Inspection Survey | Evaluate Protective Settings & Optimize for Fire Safety
Radford | SCE Feed | 522 | 522 | 0.011973 | 20 | 34.5 | 3 | High | High | 3437 | 89 | 0 | 0 | 0 | 0 | 2.82 | 0.02 | 0 | 0 | 0 | 0 | 4 | 0% | None |  | NA |  |  | NA |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Shay | SCE Feed | -169.2033 | 0 | -0.0038809 | 25 | 34.5 | 2 | Medium | High | 9582 | 586 | 0 | 24 | 0 | 1.27 | 15.9 | 0.39 | 0 | 0 | 0 | 0 | 1 | 36% | None |  | NA |  |  | 33.33% |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Baldwin | SCE Feed | 6890.98 | 6890.98 | 0.15805 | 1 | 34.5 | 2 | Medium | High | 11621 | 236 | 0 | 20 | 0 | 7.62 | 1.32 | 0.5 | 0 | 0 | 0 | 0 | 2 | 7% | None |  | NA |  |  | 0% |  | X | X | X | X | X | X | X | X | X | NA |  | X | Next WMP
Boulder | Village | 882.12 | 882.12 | 0.020232 | 16 | 4.16 | 2 | Medium | High | 2015 | 990 | 22 | 6 | 0 | 17.28 | 0.4 | 1.8 | 59 | 0 | 0 | 0 | 9 | 90% | 80.27% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
North Shore (Fawnskin) | Fawnskin | 6717.2367 | 6717.2367 | 0.15407 | 2 | 4.16 | 2 | High | High | 1512 | 924 | 0 | 0 | 0 | 15.83 | 0 | 8.09 | 54 | 0 | 0 | 0 | 3 | 0% | 79.93% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Erwin Lake | Maltby | -1118.8971 | 0 | -0.025663 | 26 | 4.16 | 2 | Medium | High | 2574 | 1054 | 2 | 6 | 0 | 13.34 | 7.99 | 7.41 | 1 | 0 | 0 | 0 | NR | 82% | [5 empty] | 82.86% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pioneer (Palomino) | Palomino | 2729.88 | 2729.88 | 0.062613 | 6 | 4.16 | 2 | Medium | High | 534 | 601 | 0 | 1 | 0 | 11.22 | 5.17 | 2.95 | 0 | 0 | 0 | 0 | NR | 20% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Clubview | Moonridge | 3010.92 | 3010.92 | 0.069059 | 5 | 4.16 | 2 | High | Medium | 1723 | 507 | 3 | 2 | 0 | 9.23 | 0.95 | 0.27 | 14 | 0 | 0 | 0 | 8 | 0% | 84.09% |  |  |  |  | 60% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Goldmine | Moonridge | 4538.8 | 4538.8 | 0.1041 | 4 | 4.16 | 2 | Medium | High | 2033 | 601 | 0 | 0 | 0 | 13.2 | 0 | 5.26 | 12 | 0 | 0 | 0 | 7 | 0% | [5 empty] | 40% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Paradise | Maltby | 1242.4667 | 1242.4667 | 0.028497 | 12 | 4.16 | 2 | Medium | High | 1874 | 532 | 3 | 17 | 0 | 6.45 | 3.4 | 2 | 0 | 0 | 0 | 0 | NR | 10% | 7.25% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunset | Maple | 2074.56 | 2074.56 | 0.047582 | 7 | 4.16 | 2 | High | Medium | 1894 | 505 | 0 | 0 | 0 | 7.64 | 3.03 | 0.5 | 50 | 0 | 0 | 0 | NR | 8% | 5.66% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunrise (Maple) | Maple | 1711.93 | 1711.93 | 0.039265 | 8 | 4.16 | 2 | Medium | Medium | 1772 | 348 | 0 | 0 | 0 | 7.17 | 0.62 | 3.86 | 34 | 0 | 0 | 0 | NR | 5% | 5.56% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Holcomb (Bear City) | Bear City | 4746.15 | 4746.15 | 0.10886 | 3 | 4.16 | 2 | Medium | High | 1581 | 609 | 2 | 4 | 0 | 13.15 | 0.1 | 0.85 | 33 | 0 | 0 | 6 | NR | 1% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Georgia | Pineknot | 1103 | 1103 | 0.025299 | 14 | 4.16 | 2 | Medium | Low | 935 | 349 | 0 | 0 | 0 | 5 | 0.91 | 3.95 | 64 | 0 | 0 | 1 | NR | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Eagle | Pineknot | 1508.5167 | 1508.5167 | 0.0346 | 9 | 4.16 | 2 | Medium | Medium | 689 | 323 | 0 | 0 | 0 | 6.65 | 0.73 | 1.53 | 0 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Harnish (Village) | Village | 786.06 | 786.06 | 0.018029 | 17 | 4.16 | 2 | Medium | Low | 327 | 86 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 11 | 0 | 0 | 0 | 6 | 0% | 15.38% |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Garstin | Meadow | 905.51 | 905.51 | 0.020769 | 15 | 4.16 | 2 | High | Low | 1347 | 277 | 0 | 0 | 0 | 3.89 | 2.02 | 3 | 15 | 0 | 0 | 0 | NR | 5% | 0% |  |  |  |  | 25% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lagonita | Village | 1453.14 | 1453.14 | 0.033329 | 11 | 4.16 | 2 | Medium | Low | 1095 | 452 | 1 | 0 | 0 | 7.46 | 0 | 1.43 | 38 | 0 | 0 | 0 | NR | 0% | 3.33% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Interlaken | Meadow | 1116.68 | 1116.68 | 0.025612 | 13 | 4.16 | 2 | Medium | Medium | 889 | 280 | 0 | 0 | 0 | 4.92 | 1.53 | 3.55 | 27 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Castle Glen (Division) | Division | 1483.32 | 1483.32 | 0.034022 | 10 | 4.16 | 2 | Medium | High | 1216 | 340 | 9 | 2 | 0 | 5.33 | 1.6 | 3.68 | 45 | 0 | 0 | 0 | 10 | 10% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Country Club | Division | 639.5367 | 639.5367 | 0.014668 | 18 | 4.16 | 2 | Medium | Medium | 596 | 178 | 1 | 0 | 0 | 3.03 | 0.15 | 0.94 | 8 | 0 | 0 | 0 | NR | 0% | 20% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Fox Farm | Meadow | -4 | 0 | -9.1744e-05 | 24 | 4.16 | 2 | Low | Low | 28 | 2 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pump House (Lake) | Lake | 201.76 | 201.76 | 0.0046276 | 21 | 4.16 | 2 | Low | High | 3 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lift (Summit TOU) | Summit | 626.9 | 626.9 | 0.014379 | 19 | 4.16 | 2 | Low | Low | 0 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 22 | 4.16 | 2 | Low | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 22 | 4.16 | 2 | Low | Low | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
|  | 43599.3662 | 44891.4667 | 1 | [6 empty] | 9892 | 43 | 82 | 0 | 161.76 | 48.64 | 54.08 | 465 | 0 | 0 | 7
|  |  | Wildfire Risk Groups | [19 empty] | Status
|  |  | High | [20 empty] | Not Started
|  |  | Moderate | [20 empty] | In Progress
|  |  | Low | [20 empty] | Complete or Implemented
Not Applicable
[15 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[15 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[14 empty] | 34 kV | 8.89 | 20.04 | 0.91 | 29.84
[14 empty] | 4 kV | 152.87 | 28.6 | 53.17 | 234.64
[14 empty] | Total | 161.76 | 48.64 | 54.08 | 264.48
[15 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[14 empty] | 34 kV | 3.361% | 7.577% | 0.3441% | 11.28%
[14 empty] | 4 kV | 57.8% | 10.81% | 20.1% | 88.72%
[14 empty] | Total | 61.16% | 18.39% | 20.45% | 100%
[15 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[14 empty] | 34 kV | 29.79% | 67.16% | 3.05%
[15 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[14 empty] | 4 kV | 65.15% | 12.19% | 22.66%

## Circuit Status 2022-12-31
Circuit Information | [22 empty] | Wildfire T&D Hardening | [9 empty] | O&M Programs Implemented
Algorithm Input = AI | [5 empty] | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI | AI | [5 empty] | AI |  | AI |  | AI | AI | AI | AI | AI | AI | AI
Circuit | Substation | Wildfire Risk Group | Wildfire Risk Group | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked) | Pole Loading Program (Percent Complete) | Tree Attachment Removal Program | Repalce OH Bare Wire with Covered Conductor | Replace Expulsion Fuses | Evacuation Route Hardening | Circuit Sectionalized to Reduce PSPS Impact | Fault Indicators | Replace AR with Pulse Conditioned Intellirupter | Circuit Meters Installed On All Phases Remotely Monitored | Install FLISR | Enhanced Vegetation Management | GO-165 Ground Patrol | GO-165 5-Year Inspections | GO-165 Intrussive Inspections | Annual LiDAR Survey | 3rd Party Annual Ground Patrol | GO-174 Substation Inspections | Substation Electrical Equipment Preventative Maintenance | Exacter Survey | Fly-over Video Inspection Survey | Evaluate Protective Settings & Optimize for Fire Safety
Radford | SCE Feed | 31214.88 | 31214.88 | 0.38264 | 1 | 34.5 | 3 | High | High | 3437 | 89 | 0 | 0 | 0 | 2.82 | 0 | 0.02 | 0 | 0 | 0 | 0 | 4 | 0% | None |  | NA |  |  | NA |  | X |  | X | X | X | X | X | X | X | NA |  | X | Next WMP
Shay | SCE Feed | 3524.4967 | 3524.4967 | 0.043204 | 6 | 34.5 | 2 | Medium | High | 9582 | 586 | 0 | 24 | 0 | 5.57 | 11.6 | 0.39 | 0 | 0 | 0 | 0 | 1 | 36% | None |  | NA |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | NA |  | X | Next WMP
Baldwin | SCE Feed | 6890.98 | 6890.98 | 0.08447 | 2 | 34.5 | 2 | Medium | High | 11621 | 236 | 0 | 20 | 0 | 7.62 | 1.32 | 0.5 | 0 | 0 | 0 | 0 | 2 | 7% | None |  | NA |  |  | 0% |  | X |  | X | X | X | X | X | X | X | NA |  | X | Next WMP
Boulder | Village | 882.12 | 882.12 | 0.010813 | 18 | 4.16 | 2 | Medium | High | 2015 | 990 | 22 | 6 | 0 | 17.28 | 0.4 | 1.8 | 59 | 0 | 0 | 0 | 9 | 90% | 80.27% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
North Shore (Fawnskin) | Fawnskin | 6717.2367 | 6717.2367 | 0.082341 | 3 | 4.16 | 2 | High | High | 1512 | 924 | 0 | 0 | 0 | 15.83 | 0 | 8.09 | 54 | 0 | 0 | 0 | 3 | 0% | 79.93% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Erwin Lake | Maltby | -246.2571 | 0 | -0.0030186 | 26 | 4.16 | 2 | Medium | High | 2574 | 1054 | 2 | 6 | 0 | 15.5 | 5.83 | 7.41 | 1 | 0 | 0 | 0 | NR | 82% | [5 empty] | 82.86% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pioneer (Palomino) | Palomino | 2729.88 | 2729.88 | 0.033463 | 8 | 4.16 | 2 | Medium | High | 534 | 601 | 0 | 1 | 0 | 11.22 | 5.17 | 2.95 | 0 | 0 | 0 | 0 | NR | 20% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Clubview | Moonridge | 3225.04 | 3225.04 | 0.039533 | 7 | 4.16 | 2 | High | Medium | 1723 | 507 | 3 | 2 | 0 | 9.76 | 0.42 | 0.27 | 14 | 0 | 0 | 0 | 8 | 0% | 84.09% |  |  |  |  | 60% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Goldmine | Moonridge | 4538.8 | 4538.8 | 0.055637 | 5 | 4.16 | 2 | Medium | High | 2033 | 601 | 0 | 0 | 0 | 13.2 | 0 | 5.26 | 12 | 0 | 0 | 0 | 7 | 0% | [5 empty] | 40% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Paradise | Maltby | 1809.5467 | 1809.5467 | 0.022182 | 12 | 4.16 | 2 | Medium | High | 1874 | 532 | 3 | 17 | 0 | 7.22 | 2.63 | 2 | 64 | 0 | 0 | 0 | NR | 10% | 7.25% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunset | Maple | 2373.52 | 2373.52 | 0.029095 | 9 | 4.16 | 2 | High | Medium | 1894 | 505 | 0 | 0 | 0 | 8.38 | 2.29 | 0.5 | 50 | 0 | 0 | 0 | NR | 8% | 5.66% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunrise (Maple) | Maple | 1856.69 | 1856.69 | 0.02276 | 10 | 4.16 | 2 | Medium | Medium | 1772 | 348 | 0 | 0 | 0 | 7.61 | 0.18 | 3.86 | 34 | 0 | 0 | 0 | NR | 5% | 5.56% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Holcomb (Bear City) | Bear City | 4746.15 | 4746.15 | 0.058179 | 4 | 4.16 | 2 | Medium | High | 1581 | 609 | 2 | 4 | 0 | 13.15 | 0.1 | 0.85 | 33 | 0 | 0 | 6 | NR | 1% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Georgia | Pineknot | 1384.19 | 1384.19 | 0.016968 | 16 | 4.16 | 2 | Medium | Low | 935 | 349 | 0 | 0 | 0 | 5.91 | 0 | 3.95 | 64 | 0 | 0 | 1 | NR | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Eagle | Pineknot | 1812.6867 | 1812.6867 | 0.02222 | 11 | 4.16 | 2 | Medium | Medium | 689 | 323 | 0 | 0 | 0 | 7.38 | 0 | 1.53 | 16 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Harnish (Village) | Village | 786.06 | 786.06 | 0.0096356 | 19 | 4.16 | 2 | Medium | Low | 327 | 86 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 11 | 0 | 0 | 0 | 6 | 0% | 15.38% |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Garstin | Meadow | 1366.31 | 1366.31 | 0.016748 | 17 | 4.16 | 2 | High | Low | 1347 | 277 | 0 | 0 | 0 | 5.09 | 0.82 | 3 | 15 | 0 | 0 | 0 | NR | 5% | 0% |  |  |  |  | 25% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lagonita | Village | 1533.14 | 1533.14 | 0.018793 | 13 | 4.16 | 2 | Medium | Low | 1095 | 452 | 1 | 0 | 0 | 7.46 | 0 | 1.43 | 58 | 0 | 0 | 0 | NR | 0% | 3.33% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Interlaken | Meadow | 1485.16 | 1485.16 | 0.018205 | 14 | 4.16 | 2 | Medium | Medium | 889 | 280 | 0 | 0 | 0 | 6.04 | 0.41 | 3.55 | 27 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Castle Glen (Division) | Division | 1483.32 | 1483.32 | 0.018183 | 15 | 4.16 | 2 | Medium | High | 1216 | 340 | 9 | 2 | 0 | 5.33 | 1.6 | 3.68 | 45 | 0 | 0 | 0 | 10 | 10% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Country Club | Division | 639.5367 | 639.5367 | 0.0078395 | 20 | 4.16 | 2 | Medium | Medium | 596 | 178 | 1 | 0 | 0 | 3.03 | 0.15 | 0.94 | 8 | 0 | 0 | 0 | NR | 0% | 20% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Fox Farm | Meadow | -4 | 0 | -4.9032e-05 | 25 | 4.16 | 2 | Low | Low | 28 | 2 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pump House (Lake) | Lake | 201.76 | 201.76 | 0.0024732 | 22 | 4.16 | 2 | Low | High | 3 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lift (Summit TOU) | Summit | 627.4 | 627.4 | 0.0076907 | 21 | 4.16 | 2 | Low | Low | 0 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 |  | X | Next WMP
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 23 | 4.16 | 2 | Low | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 | NA | NA | Next WMP
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 23 | 4.16 | 2 | Low | Low | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
|  | 81578.6462 | 81828.9033 | 1 | [6 empty] | 9892 | 43 | 82 | 0 | 177.48 | 32.92 | 54.08 | 565 | 0 | 0 | 7
|  |  | Wildfire Risk Groups | [19 empty] | Status
|  |  | High | [20 empty] | Not Started
|  |  | Moderate | [20 empty] | In Progress
|  |  | Low | [20 empty] | Complete or Implemented
Not Applicable
[15 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[15 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[14 empty] | 34 kV | 16.01 | 12.92 | 0.91 | 29.84
[14 empty] | 4 kV | 161.47 | 20 | 53.17 | 234.64
[14 empty] | Total | 177.48 | 32.92 | 54.08 | 264.48
[15 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[14 empty] | 34 kV | 6.053% | 4.885% | 0.3441% | 11.28%
[14 empty] | 4 kV | 61.05% | 7.562% | 20.1% | 88.72%
[14 empty] | Total | 67.11% | 12.45% | 20.45% | 100%
[15 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[14 empty] | 34 kV | 53.65% | 43.3% | 3.05%
[15 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[14 empty] | 4 kV | 68.82% | 8.524% | 22.66%

## Circuit Status 2022-6-30
Circuit Information | [22 empty] | Wildfire T&D Hardening | [9 empty] | O&M Programs Implemented
Algorithm Input = AI | [5 empty] | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI | AI | [5 empty] | AI |  | AI |  | AI | AI | AI | AI | AI | AI | AI
Circuit | Substation | Wildfire Risk Group | Wildfire Risk Group | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked) | Pole Loading Program (Percent Complete) | Tree Attachment Removal Program | Repalce OH Bare Wire with Covered Conductor | Replace Expulsion Fuses | Evacuation Route Hardening | Circuit Sectionalized to Reduce PSPS Impact | Fault Indicators | Replace AR with Pulse Conditioned Intellirupter | Circuit Meters Installed On All Phases Remotely Monitored | Install FLISR | Enhanced Vegetation Management | GO-165 Ground Patrol | GO-165 5-Year Inspections | GO-165 Intrussive Inspections | Annual LiDAR Survey | 3rd Party Annual Ground Patrol | GO-174 Substation Inspections | Substation Electrical Equipment Preventative Maintenance | Exacter Survey | Fly-over Video Inspection Survey | Evaluate Protective Settings & Optimize for Fire Safety
Radford | SCE Feed | 31214.88 | 31214.88 | 0.35402 | 1 | 34.5 | 3 | High | High | 3489 | 89 | 0 | 0 | 0 | 2.82 | 0 | 0.02 | 0 | 0 | 0 | 0 | 4 | 0% | None |  | NA |  |  | NA |  | X |  | X | X | X | X | X | X | X | NA |  | X | Next WMP
Shay | SCE Feed | 6122.3367 | 6122.3367 | 0.069436 | 4 | 34.5 | 2 | Medium | High | 9519 | 602 | 0 | 8 | 0 | 8.63 | 8.54 | 0.39 | 0 | 0 | 0 | 0 | 1 | 35% | None |  | NA |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | NA |  | X | Next WMP
Baldwin | SCE Feed | 6890.98 | 6890.98 | 0.078154 | 3 | 34.5 | 2 | Medium | High | 11589 | 236 | 0 | 20 | 0 | 7.62 | 1.32 | 0.5 | 0 | 0 | 0 | 0 | 2 | 7% | None |  | NA |  |  | 0% |  | X |  | X | X | X | X | X | X | X | NA |  | X | Next WMP
Boulder | Village | 962.02 | 962.02 | 0.010911 | 18 | 4.16 | 2 | Medium | High | 2051 | 991 | 21 | 6 | 0 | 17.28 | 0.4 | 1.8 | 59 | 0 | 0 | 0 | 9 | 90% | 71% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
North Shore (Fawnskin) | Fawnskin | 7721.2367 | 7721.2367 | 0.08757 | 2 | 4.16 | 2 | High | High | 1525 | 924 | 0 | 0 | 0 | 15.83 | 0 | 8.09 | 55 | 0 | 1 | 0 | 3 | 0% | 80% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Erwin Lake | Maltby | 27.1429 | 27.1429 | 0.00030784 | 23 | 4.16 | 2 | Medium | High | 2530 | 1059 | 2 | 1 | 0 | 16 | 5.83 | 7.41 | 0 | 0 | 0 | 0 | NR | 80% | [5 empty] | 82.86% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pioneer (Palomino) | Palomino | 2726.88 | 2726.88 | 0.030927 | 8 | 4.16 | 2 | Medium | High | 537 | 602 | 0 | 0 | 0 | 11.22 | 5.17 | 2.95 | 0 | 0 | 0 | 0 | NR | 20% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Clubview | Moonridge | 4656.72 | 4656.72 | 0.052814 | 6 | 4.16 | 2 | High | Medium | 1700 | 510 | 2 | 0 | 0 | 10.18 | 0 | 0.27 | 81 | 0 | 1 | 0 | 8 | 0% | 8% |  |  |  |  | 60% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Goldmine | Moonridge | 4538.8 | 4538.8 | 0.051477 | 7 | 4.16 | 2 | Medium | High | 1987 | 601 | 0 | 0 | 0 | 13.2 | 0 | 5.26 | 12 | 0 | 0 | 0 | 7 | 0% | [5 empty] | 40% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Paradise | Maltby | 2059.9067 | 2059.9067 | 0.023362 | 10 | 4.16 | 2 | Medium | High | 1895 | 532 | 3 | 17 | 0 | 7.81 | 2.04 | 2 | 67 | 0 | 0 | 0 | NR | 10% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunset | Maple | 2461.27 | 2461.27 | 0.027914 | 9 | 4.16 | 2 | High | Medium | 1918 | 505 | 0 | 0 | 0 | 8.38 | 2.29 | 0.5 | 53 | 0 | 0 | 0 | NR | 5% | 0% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunrise (Maple) | Maple | 1864.69 | 1864.69 | 0.021148 | 12 | 4.16 | 2 | Medium | Medium | 1754 | 348 | 0 | 0 | 0 | 7.61 | 0.18 | 3.86 | 36 | 0 | 0 | 0 | NR | 5% | 0% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Holcomb (Bear City) | Bear City | 4733.85 | 4733.85 | 0.053689 | 5 | 4.16 | 2 | Medium | High | 1587 | 615 | 0 | 0 | 0 | 13.15 | 0.1 | 0.85 | 33 | 0 | 0 | 6 | NR | 1% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Georgia | Pineknot | 1384.19 | 1384.19 | 0.015699 | 17 | 4.16 | 2 | Medium | Low | 945 | 349 | 0 | 0 | 0 | 5.91 | 0 | 3.95 | 64 | 0 | 0 | 1 | NR | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Eagle | Pineknot | 1812.6867 | 1812.6867 | 0.020559 | 13 | 4.16 | 2 | Medium | Medium | 676 | 323 | 0 | 0 | 0 | 7.38 | 0 | 1.53 | 16 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Harnish (Village) | Village | 792.76 | 792.76 | 0.0089911 | 19 | 4.16 | 2 | Medium | Low | 332 | 86 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 11 | 0 | 0 | 0 | 6 | 0% | 15% |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Garstin | Meadow | 1391.76 | 1391.76 | 0.015785 | 16 | 4.16 | 2 | High | Low | 1338 | 277 | 0 | 0 | 0 | 5.09 | 0.82 | 3 | 15 | 0 | 0 | 0 | NR | 5% | 0% |  |  |  |  | 25% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Lagonita | Village | 1576.44 | 1576.44 | 0.017879 | 15 | 4.16 | 2 | Medium | Low | 1106 | 453 | 0 | 0 | 0 | 7.46 | 0 | 1.43 | 60 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Interlaken | Meadow | 1652.3 | 1652.3 | 0.018739 | 14 | 4.16 | 2 | Medium | Medium | 880 | 280 | 0 | 0 | 0 | 6.45 | 0 | 3.55 | 27 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Castle Glen (Division) | Division | 2043.26 | 2043.26 | 0.023174 | 11 | 4.16 | 2 | Medium | High | 1189 | 341 | 9 | 1 | 0 | 6.64 | 0.29 | 3.68 | 45 | 0 | 0 | 0 | 10 | 10% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Country Club | Division | 712.7867 | 712.7867 | 0.008084 | 20 | 4.16 | 2 | Medium | Medium | 605 | 178 | 1 | 0 | 0 | 3.18 | 0 | 0.94 | 10 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Fox Farm | Meadow | -4 | 0 | -4.5366e-05 | 26 | 4.16 | 2 | Low | Low | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Pump House (Lake) | Lake | 201.76 | 201.76 | 0.0022883 | 22 | 4.16 | 2 | Low | High | 4 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lift (Summit TOU) | Summit | 627.4 | 627.4 | 0.0071156 | 21 | 4.16 | 2 | Low | Low | 1 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 |  | X | Next WMP
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 24 | 4.16 | 2 | Low | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 | NA | NA | Next WMP
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 24 | 4.16 | 2 | Low | Low | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
|  | 88172.0562 | 88176.0562 | 1 | [6 empty] | 9926 | 38 | 53 | 0 | 183.92 | 26.98 | 54.08 | 644 | 0 | 2 | 7
|  |  | Wildfire Risk Groups | [19 empty] | Status
|  |  | High | [20 empty] | Not Started
|  |  | Moderate | [20 empty] | In Progress
|  |  | Low | [20 empty] | Complete or Implemented
Not Applicable
[15 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[15 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[14 empty] | 34 kV | 19.07 | 9.86 | 0.91 | 29.84
[14 empty] | 4 kV | 164.85 | 17.12 | 53.17 | 235.14
[14 empty] | Total | 183.92 | 26.98 | 54.08 | 264.98
[15 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[14 empty] | 34 kV | 7.197% | 3.721% | 0.3434% | 11.26%
[14 empty] | 4 kV | 62.21% | 6.461% | 20.07% | 88.74%
[14 empty] | Total | 69.41% | 10.18% | 20.41% | 100%
[15 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[14 empty] | 34 kV | 63.91% | 33.04% | 3.05%
[15 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[14 empty] | 4 kV | 70.11% | 7.281% | 22.61%

## Circuit Status 2021-12-31
Circuit Information | [22 empty] | Wildfire T&D Hardening | [9 empty] | O&M Programs Implemented
Algorithm Input = AI | [5 empty] | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI | AI | [5 empty] | AI |  | AI |  | AI | AI | AI | AI | AI | AI | AI
Circuit | Substation | Wildfire Risk Group | Wildfire Risk Group | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked) | Pole Loading Program (Percent Complete) | Tree Attachment Removal Program | Repalce OH Bare Wire with Covered Conductor | Replace Expulsion Fuses | Evacuation Route Hardening | Circuit Sectionalized to Reduce PSPS Impact | Fault Indicators | Replace AR with Pulse Conditioned Intellirupter | Circuit Meters Installed On All Phases Remotely Monitored | Install FLISR | Enhanced Vegetation Management | GO-165 Ground Patrol | GO-165 5-Year Inspections | GO-165 Intrussive Inspections | Annual LiDAR Survey | 3rd Party Annual Ground Patrol | GO-174 Substation Inspections | Substation Electrical Equipment Preventative Maintenance | Exacter Survey | Fly-over Video Inspection Survey | Evaluate Protective Settings & Optimize for Fire Safety
Radford | SCE Feed | 31214.88 | 31214.88 | 0.34537 | 1 | 34.5 | 3 | High | High | 3482 | 89 | 0 | 0 | 0 | 2.82 | 0 | 0.02 | 0 | 0 | 0 | 0 | 4 | 0% | None |  | NA |  |  | NA |  | X |  | X | X | X | X | X | X | X | NA |  | X | Next WMP
Shay | SCE Feed | 7102.5967 | 7102.5967 | 0.078585 | 3 | 34.5 | 2 | Medium | High | 9521 | 609 | 0 | 1 | 0 | 9.27 | 7.9 | 0.39 | 0 | 0 | 0 | 0 | 1 | 20% | None |  | NA |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | NA |  | X | Next WMP
Baldwin | SCE Feed | 7606.01 | 7606.01 | 0.084154 | 2 | 34.5 | 2 | Medium | High | 11584 | 253 | 0 | 3 | 0 | 8.44 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 2 | 3% | None |  | NA |  |  | 0% |  | X |  | X | X | X | X | X | X | X | NA |  | X | Next WMP
Boulder | Village | 1229.62 | 1229.62 | 0.013605 | 19 | 4.16 | 2 | Medium | High | 2046 | 1007 | 0 | 1 | 0 | 17.68 | 0 | 1.8 | 86 | 0 | 0 | 1 | 9 | 90% | 71% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
North Shore (Fawnskin) | Fawnskin | 6721.2367 | 6721.2367 | 0.074365 | 4 | 4.16 | 2 | High | High | 1523 | 924 | 0 | 0 | 0 | 15.83 | 0 | 8.09 | 55 | 0 | 0 | 0 | 3 | 0% | 80% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Erwin Lake | Maltby | 2005.5429 | 2005.5429 | 0.02219 | 13 | 4.16 | 2 | Medium | High | 2533 | 1060 | 0 | 0 | 0 | 19.6 | 2.23 | 7.41 | 0 | 0 | 0 | 0 | NR | 70% | [5 empty] | 82.86% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Pioneer (Palomino) | Palomino | 2425.88 | 2425.88 | 0.02684 | 10 | 4.16 | 2 | Medium | High | 537 | 602 | 0 | 0 | 0 | 11.22 | 5.17 | 2.95 | 0 | 0 | 0 | 0 | NR | 30% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Clubview | Moonridge | 3330.72 | 3330.72 | 0.036852 | 7 | 4.16 | 2 | High | Medium | 1698 | 511 | 0 | 0 | 0 | 10.18 | 0 | 0.27 | 0 | 0 | 0 | 0 | 8 | 0% | 8% |  |  |  |  | 60% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Goldmine | Moonridge | 4490.8 | 4490.8 | 0.049687 | 5 | 4.16 | 2 | Medium | High | 1984 | 601 | 0 | 0 | 0 | 13.2 | 0 | 5.26 | 0 | 0 | 0 | 0 | 7 | 0% | [5 empty] | 40% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Paradise | Maltby | 2894.4467 | 2894.4467 | 0.032025 | 8 | 4.16 | 2 | Medium | High | 1895 | 549 | 0 | 0 | 0 | 9.17 | 0.68 | 2 | 69 | 0 | 0 | 1 | NR | 2% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunset | Maple | 2533.02 | 2533.02 | 0.028026 | 9 | 4.16 | 2 | High | Medium | 1918 | 505 | 0 | 0 | 0 | 8.38 | 2.29 | 0.5 | 52 | 0 | 0 | 0 | NR | 2% | 0% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Sunrise (Maple) | Maple | 2216.89 | 2216.89 | 0.024528 | 12 | 4.16 | 2 | Medium | Medium | 1506 | 348 | 0 | 0 | 0 | 7.61 | 0.18 | 3.86 | 36 | 0 | 0 | 3 | NR | 2% | 0% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Holcomb (Bear City) | Bear City | 4205 | 4205 | 0.046525 | 6 | 4.16 | 2 | Medium | High | 1587 | 615 | 0 | 0 | 0 | 13.25 | 0 | 0.85 | 33 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Georgia | Pineknot | 1280.19 | 1280.19 | 0.014164 | 18 | 4.16 | 2 | Medium | Low | 945 | 349 | 0 | 0 | 0 | 5.91 | 0 | 3.95 | 63 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Eagle | Pineknot | 1812.6867 | 1812.6867 | 0.020056 | 14 | 4.16 | 2 | Medium | Medium | 959 | 323 | 0 | 0 | 0 | 7.38 | 0 | 1.53 | 16 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Harnish (Village) | Village | 792.76 | 792.76 | 0.0087713 | 20 | 4.16 | 2 | Medium | Low | 254 | 86 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 11 | 0 | 0 | 0 | 6 | 0% | 15% |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Garstin | Meadow | 1391.76 | 1391.76 | 0.015399 | 17 | 4.16 | 2 | High | Low | 1055 | 277 | 0 | 0 | 0 | 5.09 | 0.82 | 3 | 15 | 0 | 0 | 0 | NR | 5% | 0% |  |  |  |  | 25% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Lagonita | Village | 1576.44 | 1576.44 | 0.017442 | 16 | 4.16 | 2 | Medium | Low | 1103 | 453 | 0 | 0 | 0 | 7.46 | 0 | 1.43 | 60 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Interlaken | Meadow | 1652.3 | 1652.3 | 0.018281 | 15 | 4.16 | 2 | Medium | Medium | 880 | 280 | 0 | 0 | 0 | 6.45 | 0 | 3.55 | 27 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Castle Glen (Division) | Division | 2364.91 | 2364.91 | 0.026166 | 11 | 4.16 | 2 | Medium | High | 1188 | 343 | 8 | 0 | 0 | 6.74 | 0.19 | 3.68 | 45 | 0 | 0 | 2 | 10 | 5% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Country Club | Division | 708.7867 | 708.7867 | 0.0078422 | 21 | 4.16 | 2 | Medium | Medium | 605 | 180 | 0 | 0 | 0 | 3.18 | 0 | 0.94 | 10 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Fox Farm | Meadow | -4 | 0 | -4.4257e-05 | 26 | 4.16 | 2 | Low | Low | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2022 |  | X | Next WMP
Pump House (Lake) | Lake | 201.76 | 201.76 | 0.0022323 | 23 | 4.16 | 2 | Low | High | 4 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | X |  | X | Next WMP
Lift (Summit TOU) | Summit | 627.4 | 627.4 | 0.0069417 | 22 | 4.16 | 2 | Low | Low | 1 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 |  | X | Next WMP
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 24 | 4.16 | 2 | Low | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 | NA | NA | Next WMP
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 24 | 4.16 | 2 | Low | Low | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | X | NA | NA | Next WMP
|  | 90381.6362 | 90385.6362 | 1 | [6 empty] | 9989 | 8 | 5 | 0 | 190.94 | 19.96 | 54.08 | 578 | 0 | 0 | 7
|  |  | Wildfire Risk Groups | [19 empty] | Status
|  |  | High | [20 empty] | Not Started
|  |  | Moderate | [20 empty] | In Progress
|  |  | Low | [20 empty] | Complete or Implemented
Not Applicable
[15 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[15 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[14 empty] | 34 kV | 20.53 | 8.4 | 0.91 | 29.84
[14 empty] | 4 kV | 170.41 | 11.56 | 53.17 | 235.14
[14 empty] | Total | 190.94 | 19.96 | 54.08 | 264.98
[15 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[14 empty] | 34 kV | 7.748% | 3.17% | 0.3434% | 11.26%
[14 empty] | 4 kV | 64.31% | 4.363% | 20.07% | 88.74%
[14 empty] | Total | 72.06% | 7.533% | 20.41% | 100%
[15 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[14 empty] | 34 kV | 68.8% | 28.15% | 3.05%
[15 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[14 empty] | 4 kV | 72.47% | 4.916% | 22.61%

## Circuit Status 2021-6-30
Circuit Information | [22 empty] | Wildfire T&D Hardening | [9 empty] | O&M Programs Implemented
Algorithm Input = AI | [5 empty] | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI | AI | [5 empty] | AI |  | AI |  | AI | AI | AI | AI | AI | AI | AI
Circuit | Substation | Wildfire Risk Group | Wildfire Risk Group | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked) | Pole Loading Program (Percent Complete) | Tree Attachment Removal Program | Repalce OH Bare Wire with Covered Conductor | Replace Expulsion Fuses | Evacuation Route Hardening | Circuit Sectionalized to Reduce PSPS Impact | Fault Indicators | Replace AR with Pulse Conditioned Intellirupter | Circuit Meters Installed On All Phases Remotely Monitored | Install FLISR | Enhanced Vegetation Management | GO-165 Ground Patrol | GO-165 5-Year Inspections | GO-165 Intrussive Inspections | Annual LiDAR Survey | 3rd Party Annual Ground Patrol | GO-174 Substation Inspections | Substation Electrical Equipment Preventative Maintenance | Exacter Survey | Fly-over Video Inspection Survey | Evaluate Protective Settings & Optimize for Fire Safety
Radford | SCE Feed | 30520.52 | 30520.52 | 0.31803 | 1 | 34.5 | 3 | High | High | 3482 | 89 | 0 | 0 | 0 | 2.82 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR | 0% | None |  | NA |  |  | NA |  | X |  | X | X | X | X | X | X | X | NA |  | Next WMP | Next WMP
Shay | SCE Feed | 6670.6367 | 6670.6367 | 0.069509 | 3 | 34.5 | 2 | Medium | High | 9521 | 610 | 0 | 0 | 0 | 9.27 | 7.9 | 0.39 | 0 | 0 | 0 | 0 | 7 | 15% | None |  | NA |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | NA |  | Next WMP | Next WMP
Baldwin | SCE Feed | 7516.44 | 7516.44 | 0.078323 | 2 | 34.5 | 2 | Medium | High | 11584 | 256 | 0 | 0 | 0 | 8.44 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 3 | 3% | None |  | NA |  |  | 0% |  | X |  | X | X | X | X | X | X | X | NA |  | Next WMP | Next WMP
Boulder | Village | 3284.48 | 3284.48 | 0.034225 | 8 | 4.16 | 2 | High | High | 2050 | 1008 | 0 | 0 | 0 | 17.68 | 0 | 1.8 | 86 | 0 | 0 | 1 | 2 | 90% | 71.23% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
North Shore (Fawnskin) | Fawnskin | 6534.0467 | 6534.0467 | 0.068086 | 5 | 4.16 | 2 | High | High | 1524 | 923 | 0 | 0 | 0 | 15.83 | 0 | 8.09 | 55 | 0 | 0 | 0 | 6 | 0% | 79.55% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X |  |  | Next WMP | Next WMP
Erwin Lake | Maltby | 1652.7429 | 1652.7429 | 0.017222 | 18 | 4.16 | 2 | Medium | High | 2529 | 1058 | 0 | 0 | 0 | 19.6 | 2.23 | 7.41 | 7 | 0 | 0 | 0 | NR | 80% | 76.67% |  |  |  |  | 82.86% |  | X |  | X | X | X | X | X | X | X |  |  | Next WMP | Next WMP
Pioneer (Palomino) | Palomino | 3005.42 | 3005.42 | 0.031317 | 10 | 4.16 | 2 | Medium | High | 539 | 602 | 0 | 0 | 0 | 11.22 | 5.17 | 2.95 | 0 | 0 | 0 | 0 | 9 | 20% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Clubview | Moonridge | 3759.98 | 3759.98 | 0.03918 | 7 | 4.16 | 2 | High | Medium | 1700 | 508 | 0 | 0 | 0 | 10.18 | 0 | 0.27 | 88 | 0 | 0 | 0 | 8 | 0% | 0% |  |  |  |  | 60% |  |  |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Goldmine | Moonridge | 6639.2 | 6639.2 | 0.069182 | 4 | 4.16 | 2 | High | High | 1987 | 568 | 0 | 0 | 0 | 13.2 | 0 | 5.26 | 75 | 0 | 0 | 1 | 1 | 0% | 18.47% |  |  |  |  | 40% |  |  |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Paradise | Maltby | 3013.5367 | 3013.5367 | 0.031402 | 9 | 4.16 | 2 | Medium | High | 1893 | 549 | 0 | 0 | 0 | 9.17 | 0.68 | 2 | 69 | 0 | 0 | 1 | NR | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X |  |  | Next WMP | Next WMP
Sunset | Maple | 2642.18 | 2642.18 | 0.027532 | 11 | 4.16 | 2 | High | Medium | 1918 | 505 | 0 | 0 | 0 | 8.38 | 2.29 | 0.5 | 52 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Sunrise (Maple) | Maple | 2575.71 | 2575.71 | 0.026839 | 12 | 4.16 | 2 | High | Medium | 1754 | 348 | 0 | 0 | 0 | 7.61 | 0.18 | 3.86 | 36 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 0% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Holcomb (Bear City) | Bear City | 4297.75 | 4297.75 | 0.044783 | 6 | 4.16 | 2 | Medium | High | 1587 | 615 | 0 | 0 | 0 | 13.25 | 0 | 0.85 | 33 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Georgia | Pineknot | 1766.81 | 1766.81 | 0.01841 | 17 | 4.16 | 2 | High | Low | 945 | 348 | 0 | 0 | 0 | 5.91 | 0 | 3.95 | 63 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Eagle | Pineknot | 1864.3467 | 1864.3467 | 0.019427 | 16 | 4.16 | 2 | Medium | Medium | 676 | 323 | 0 | 0 | 0 | 7.38 | 0 | 1.53 | 16 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 33.33% |  |  |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Harnish (Village) | Village | 897.44 | 897.44 | 0.0093515 | 20 | 4.16 | 2 | Medium | Low | 332 | 85 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 11 | 0 | 0 | 0 | 5 | 0% | 15.38% |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Garstin | Meadow | 1501.94 | 1501.94 | 0.01565 | 19 | 4.16 | 2 | High | Low | 1338 | 277 | 0 | 0 | 0 | 5.09 | 0.82 | 3 | 15 | 0 | 0 | 1 | NR | 5% | 0% |  |  |  |  | 25% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Lagonita | Village | 2291.36 | 2291.36 | 0.023876 | 13 | 4.16 | 2 | Medium | Low | 1100 | 453 | 0 | 0 | 0 | 7.46 | 0 | 1.43 | 60 | 0 | 0 | 0 | 4 | 0% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Interlaken | Meadow | 2148.95 | 2148.95 | 0.022392 | 15 | 4.16 | 2 | High | Medium | 880 | 280 | 0 | 0 | 0 | 6.45 | 0 | 3.55 | 27 | 0 | 0 | 0 | NR | 0% | 0% |  |  |  |  | 50% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Castle Glen (Division) | Division | 2278.39 | 2278.39 | 0.023741 | 14 | 4.16 | 2 | Medium | High | 1189 | 343 | 8 | 0 | 0 | 6.74 | 0.19 | 3.68 | 45 | 0 | 0 | 2 | NR | 5% | 0% |  |  |  |  | 100% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Country Club | Division | 815.1467 | 815.1467 | 0.008494 | 21 | 4.16 | 2 | Medium | Medium | 605 | 180 | 0 | 0 | 0 | 3.18 | 0 | 0.94 | 10 | 0 | 0 | 0 | 10 | 0% | 0% |  |  |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Fox Farm | Meadow | -4 | 0 | -4.1681e-05 | 26 | 4.16 | 2 | Low | Low | 35 | 2 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Pump House (Lake) | Lake | 267.04 | 267.04 | 0.0027826 | 22 | 4.16 | 2 | High | High | 4 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X |  |  | Next WMP | Next WMP
Lift (Summit TOU) | Summit | 27.6 | 27.6 | 0.0002876 | 23 | 4.16 | 2 | Low | Low | 1 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 0% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 24 | 4.16 | 2 | Low | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 | NA | NA | Next WMP
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 24 | 4.16 | 2 | Low | Low | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2022 | NA | NA | Next WMP
|  | 95967.6662 | 95971.6662 | 1 | [6 empty] | 9953 | 8 | 0 | 0 | 190.94 | 19.96 | 54.08 | 748 | 0 | 0 | 6
|  | Wildfire Risk Groups | [20 empty] | Status
|  | High | [21 empty] | Not Started
|  | Moderate | [21 empty] | In Progress
|  | Low | [21 empty] | Complete or Implemented
Not Applicable
[15 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[15 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[14 empty] | 34 kV | 20.53 | 8.4 | 0.91 | 29.84
[14 empty] | 4 kV | 170.41 | 11.56 | 53.17 | 235.14
[14 empty] | Total | 190.94 | 19.96 | 54.08 | 264.98
[15 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[14 empty] | 34 kV | 7.748% | 3.17% | 0.3434% | 11.26%
[14 empty] | 4 kV | 64.31% | 4.363% | 20.07% | 88.74%
[14 empty] | Total | 72.06% | 7.533% | 20.41% | 100%
[15 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[14 empty] | 34 kV | 68.8% | 28.15% | 3.05%
[15 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[14 empty] | 4 kV | 72.47% | 4.916% | 22.61%

## Circuit Status 2020-12-31
Circuit Information | [22 empty] | Wildfire T&D Hardening | [9 empty] | O&M Programs Implemented
Algorithm Input = AI | [5 empty] | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI | AI | [5 empty] | AI |  | AI |  | AI | AI | AI | AI | AI | AI | AI
Circuit | Substation | Wildfire Risk Group | Wildfire Risk Group | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked) | Pole Loading Program (Percent Complete) | Tree Attachment Removal Program | Repalce OH Bare Wire with Covered Conductor | Replace Expulsion Fuses | Evacuation Route Hardening | Circuit Sectionalized to Reduce PSPS Impact | Fault Indicators | Replace AR with Pulse Conditioned Intellirupter | Circuit Meters Installed On All Phases Remotely Monitored | Install FLISR | Enhanced Vegetation Management | GO-165 Ground Patrol | GO-165 5-Year Inspections | GO-165 Intrussive Inspections | Bi-Annual LiDAR Survey | 3rd Party Annual Ground Patrol | GO-174 Substation Inspections | Substation Electrical Equipment Preventative Maintenance | Exacter Survey | Fly-over Video Inspection Survey | Evaluate Protective Settings & Optimize for Fire Safety
Radford | SCE Feed | 30620.52 | 30620.52 | 0.27652 | 1 | 34.5 | 3 | High | High | 3403 | 89 | 0 | 0 | 0 | 2.82 | 0 | 0.02 | 0 | 0 | 0 | 1 | NR | 0% | None |  | NA |  |  | NA |  | X |  | X | X | X | X | X | X | X | NA |  | Next WMP | Next WMP
Shay | SCE Feed | 13366.5167 | 13366.5167 | 0.12071 | 2 | 34.5 | 2 | Medium | High | 9627 | 610 | 0 | 0 | 0 | 16.35 | 2.07 | 0.39 | 0 | 0 | 0 | 2 | 3 | 15% | None |  | NA |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | NA |  | Next WMP | Next WMP
Baldwin | SCE Feed | 7762.81 | 7762.81 | 0.070101 | 3 | 34.5 | 2 | Medium | High | 11305 | 256 | 0 | 0 | 0 | 8.61 | 0.33 | 0.5 | 0 | 0 | 0 | 0 | 2 | 3% | None |  | NA |  |  | 0% |  | X |  | X | X | X | X | X | X | X | NA |  | Next WMP | Next WMP
Boulder | Village | 2950.98 | 2950.98 | 0.026649 | 12 | 4.16 | 2 | High | High | 2046 | 1007 | 0 | 0 | 0 | 17.68 | 0 | 1.8 | 86 | 30 | 0 | 0 | 5 | 90% | [5 empty] | 100% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
North Shore (Fawnskin) | Fawnskin | 7538.0467 | 7538.0467 | 0.068072 | 4 | 4.16 | 2 | High | High | 1523 | 923 | 0 | 0 | 0 | 15.83 | 0 | 8.09 | 56 | 0 | 0 | 10 | 6 | 0% | [5 empty] | 33.33% |  | X |  | X | X | X | X | X | X | X |  |  | Next WMP | Next WMP
Erwin Lake | Maltby | 3415.6729 | 3415.6729 | 0.030845 | 11 | 4.16 | 2 | Medium | High | 2533 | 1058 | 0 | 0 | 0 | 21.83 | 0 | 7.41 | 7 | 0 | 0 | 0 | NR | 64% | [5 empty] | 82.86% |  | X |  | X | X | X | X | X | X | X |  |  | Next WMP | Next WMP
Pioneer (Palomino) | Palomino | 5206.29 | 5206.29 | 0.047015 | 6 | 4.16 | 2 | Medium | High | 537 | 602 | 0 | 0 | 0 | 16.39 | 1.25 | 2.95 | 0 | 38 | 0 | 2 | NR | 20% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Clubview | Moonridge | 4059.98 | 4059.98 | 0.036663 | 8 | 4.16 | 2 | High | Medium | 1984 | 508 | 0 | 0 | 0 | 10.18 | 0 | 0.27 | 88 | 0 | 0 | 4 | 9 | 0% | [5 empty] | 60% |  |  |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Goldmine | Moonridge | 6659.2 | 6659.2 | 0.060135 | 5 | 4.16 | 2 | High | High | 1698 | 567 | 0 | 0 | 0 | 13.2 | 0 | 5.26 | 76 | 7 | 0 | 1 | 1 | 0% | [5 empty] | 40% |  |  |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Paradise | Maltby | 3493.0167 | 3493.0167 | 0.031543 | 10 | 4.16 | 2 | Medium | High | 1895 | 549 | 0 | 0 | 0 | 9.85 | 0 | 2 | 69 | 0 | 0 | 0 | 8 | 0% | [5 empty] | 33.33% |  | X |  | X | X | X | X | X | X | X |  |  | Next WMP | Next WMP
Sunset | Maple | 3883.37 | 3883.37 | 0.035068 | 9 | 4.16 | 2 | High | Medium | 1918 | 505 | 0 | 0 | 0 | 10.67 | 0 | 0.5 | 52 | 0 | 0 | 3 | NR | 0% | [5 empty] | 0% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Sunrise (Maple) | Maple | 2649.69 | 2649.69 | 0.023928 | 13 | 4.16 | 2 | High | Medium | 1506 | 348 | 0 | 0 | 0 | 7.79 | 0 | 3.86 | 36 | 0 | 0 | 0 | NR | 0% | [5 empty] | 0% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Holcomb (Bear City) | Bear City | 4515.75 | 4515.75 | 0.040779 | 7 | 4.16 | 2 | Medium | High | 1587 | 615 | 0 | 0 | 0 | 13.25 | 0 | 0.85 | 33 | 109 | 0 | 0 | NR | 0% | [5 empty] | 50% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Georgia | Pineknot | 2018.81 | 2018.81 | 0.018231 | 18 | 4.16 | 2 | High | Low | 1023 | 348 | 0 | 0 | 0 | 5.91 | 0 | 3.95 | 63 | 76 | 0 | 1 | NR | 0% | [5 empty] | 100% |  |  |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Eagle | Pineknot | 2072.3467 | 2072.3467 | 0.018714 | 17 | 4.16 | 2 | Medium | Medium | 959 | 323 | 0 | 0 | 0 | 7.38 | 0 | 1.53 | 16 | 104 | 0 | 0 | NR | 0% | [5 empty] | 33.33% |  |  |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Harnish (Village) | Village | 585.44 | 585.44 | 0.0052868 | 21 | 4.16 | 2 | Medium | Low | 254 | 83 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 13 | 38 | 0 | 2 | NR | 0% | [5 empty] | NA |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Garstin | Meadow | 1749.94 | 1749.94 | 0.015803 | 19 | 4.16 | 2 | High | Low | 1055 | 277 | 0 | 0 | 0 | 5.09 | 0.82 | 3 | 15 | 124 | 0 | 1 | NR | 5% | [5 empty] | 25% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Lagonita | Village | 2323.36 | 2323.36 | 0.020981 | 15 | 4.16 | 2 | Medium | Low | 1103 | 453 | 0 | 0 | 0 | 7.46 | 0 | 1.43 | 60 | 116 | 0 | 1 | 7 | 0% | [5 empty] | 100% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Interlaken | Meadow | 2474.95 | 2474.95 | 0.02235 | 14 | 4.16 | 2 | High | Medium | 880 | 280 | 0 | 0 | 0 | 6.45 | 0 | 3.55 | 27 | 113 | 0 | 1 | NR | 0% | [5 empty] | 50% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Castle Glen (Division) | Division | 2238.39 | 2238.39 | 0.020214 | 16 | 4.16 | 2 | Medium | High | 1188 | 343 | 9 | 0 | 0 | 6.74 | 0.19 | 3.68 | 45 | 80 | 0 | 0 | NR | 5% | [5 empty] | 100% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Country Club | Division | 845.1467 | 845.1467 | 0.007632 | 20 | 4.16 | 2 | Medium | Medium | 605 | 180 | 0 | 0 | 0 | 3.18 | 0 | 0.94 | 10 | 15 | 0 | 0 | 10 | 0% | [5 empty] | 33.33% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Fox Farm | Meadow | -8 | 0 | -7.2243e-05 | 26 | 4.16 | 2 | Low | Low | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Pump House (Lake) | Lake | 287.04 | 287.04 | 0.0025921 | 22 | 4.16 | 2 | High | High | 4 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 10 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X |  |  | Next WMP | Next WMP
Lift (Summit TOU) | Summit | 27.6 | 27.6 | 0.00024924 | 23 | 4.16 | 2 | Low | Low | 1 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 0% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 24 | 4.16 | 2 | Low | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 | NA | NA | Next WMP
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 24 | 4.16 | 2 | Low | Low | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2022 | NA | NA | Next WMP
|  | 110736.8662 | 110744.8662 | 1 | [6 empty] | 9951 | 9 | 0 | 0 | 208.74 | 4.66 | 54.08 | 752 | 860 | 0 | 29
|  | Wildfire Risk Groups | [20 empty] | Status
|  | High | [21 empty] | Not Started
|  | Moderate | [21 empty] | In Progress
|  | Low | [21 empty] | Complete or Implemented
Not Applicable
[15 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[15 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[14 empty] | 34 kV | 27.78 | 2.4 | 0.91 | 31.09
[14 empty] | 4 kV | 180.96 | 2.26 | 53.17 | 236.39
[14 empty] | Total | 208.74 | 4.66 | 54.08 | 267.48
[15 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[14 empty] | 34 kV | 10.39% | 0.8973% | 0.3402% | 11.62%
[14 empty] | 4 kV | 67.65% | 0.8449% | 19.88% | 88.38%
[14 empty] | Total | 78.04% | 1.742% | 20.22% | 100%
[15 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[14 empty] | 34 kV | 89.35% | 7.72% | 2.927%
[15 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[14 empty] | 4 kV | 76.55% | 0.956% | 22.49%

## Circuit Status 2019-12-31
Circuit Information | [22 empty] | Wildfire T&D Hardening | [9 empty] | O&M Programs Implemented
Algorithm Input = AI | [5 empty] | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI | AI | [5 empty] | AI |  | AI |  | AI | AI | AI | AI | AI | AI | AI
Circuit | Substation | Wildfire Risk Group | Wildfire Risk Group | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked) | Pole Loading Program (Percent Complete) | Tree Attachment Removal Program | Repalce OH Bare Wire with Covered Conductor | Replace Expulsion Fuses | Evacuation Route Hardening | Circuit Sectionalized to Reduce PSPS Impact | Fault Indicators | Replace AR with Pulse Conditioned Intellirupter | Circuit Meters Installed On All Phases Remotely Monitored | Install FLISR | Enhanced Vegetation Management | GO-165 Ground Patrol | GO-165 5-Year Inspections | GO-165 Intrussive Inspections | Bi-Annual LiDAR Survey | 3rd Party Annual Ground Patrol | GO-174 Substation Inspections | Substation Electrical Equipment Preventative Maintenance | Exacter Survey | Fly-over Video Inspection Survey | Evaluate Protective Settings & Optimize for Fire Safety
Radford | SCE Feed | 30520.52 | 30520.52 | 0.2632 | 1 | 34.5 | 3 | High | High | 3403 | 89 | 0 | 0 | 0 | 2.82 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR | 0% | None |  | NA |  |  | NA |  | X |  | X | X | X | X | X | X | X | NA |  | Next WMP | Next WMP
Shay | SCE Feed | 14230.0367 | 14230.0367 | 0.12271 | 2 | 34.5 | 2 | Medium | High | 9627 | 610 | 0 | 0 | 0 | 17.17 | 0 | 0.39 | 0 | 0 | 0 | 0 | 4 | 0% | None |  | NA |  |  | 33.33% |  | X |  | X | X | X | X | X | X | X | NA |  | Next WMP | Next WMP
Baldwin | SCE Feed | 7185.34 | 7185.34 | 0.061963 | 5 | 34.5 | 2 | Medium | High | 11305 | 256 | 0 | 0 | 0 | 8.94 | 0 | 0.5 | 0 | 0 | 0 | 0 | NR | 0% | None |  | NA |  |  | 0% |  | X |  | X | X | X | X | X | X | X | NA |  | Next WMP | Next WMP
Boulder | Village | 3350.98 | 3350.98 | 0.028897 | 12 | 4.16 | 2 | High | High | 2046 | 1007 | 0 | 0 | 0 | 17.68 | 0 | 1.8 | 86 | 30 | 0 | 0 | 1 | 90% | [5 empty] | 100% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
North Shore (Fawnskin) | Fawnskin | 7518.0467 | 7518.0467 | 0.064833 | 3 | 4.16 | 2 | High | High | 1523 | 923 | 0 | 0 | 0 | 15.83 | 0 | 8.09 | 120 | 362 | 0 | 0 | 6 | 0% | [5 empty] | 33.33% |  | X |  | X | X | X | X | X | X | X | 2020 |  | Next WMP | Next WMP
Erwin Lake | Maltby | 7401.2729 | 7401.2729 | 0.063826 | 4 | 4.16 | 2 | Medium | High | 2533 | 1058 | 0 | 0 | 0 | 21.83 | 0 | 7.41 | 7 | 0 | 0 | 0 | 5 | 0% | [5 empty] | 82.86% |  | X |  | X | X | X | X | X | X | X | 2020 |  | Next WMP | Next WMP
Pioneer (Palomino) | Palomino | 5706.29 | 5706.29 | 0.049209 | 7 | 4.16 | 2 | Medium | High | 537 | 602 | 0 | 0 | 0 | 16.39 | 0 | 2.95 | 0 | 388 | 0 | 0 | NR | 20% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Clubview | Moonridge | 3459.98 | 3459.98 | 0.029837 | 11 | 4.16 | 2 | High | Medium | 1984 | 508 | 0 | 0 | 0 | 10.18 | 0 | 0.27 | 88 | 0 | 0 | 0 | NR | 0% | [5 empty] | 60% |  |  |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Goldmine | Moonridge | 5559.2 | 5559.2 | 0.04794 | 8 | 4.16 | 2 | High | High | 1698 | 567 | 0 | 0 | 0 | 13.2 | 0 | 5.26 | 76 | 7 | 0 | 0 | NR | 0% | [5 empty] | 40% |  |  |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Paradise | Maltby | 3493.0167 | 3493.0167 | 0.030122 | 10 | 4.16 | 2 | Medium | High | 1895 | 549 | 0 | 0 | 0 | 9.85 | 0 | 2 | 69 | 0 | 0 | 0 | 8 | 0% | [5 empty] | 33.33% |  | X |  | X | X | X | X | X | X | X | 2020 |  | Next WMP | Next WMP
Sunset | Maple | 3583.37 | 3583.37 | 0.030902 | 9 | 4.16 | 2 | High | Medium | 1918 | 505 | 0 | 0 | 0 | 10.67 | 0 | 0.5 | 52 | 0 | 0 | 0 | NR | 0% | [5 empty] | 0% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Sunrise (Maple) | Maple | 2649.69 | 2649.69 | 0.02285 | 14 | 4.16 | 2 | High | Medium | 1506 | 348 | 0 | 0 | 0 | 7.79 | 0 | 3.86 | 36 | 0 | 0 | 0 | NR | 0% | [5 empty] | 0% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Holcomb (Bear City) | Bear City | 5915.75 | 5915.75 | 0.051015 | 6 | 4.16 | 2 | Medium | High | 1587 | 615 | 0 | 0 | 0 | 13.25 | 0 | 0.85 | 33 | 409 | 0 | 0 | 3 | 0% | [5 empty] | 50% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Georgia | Pineknot | 1918.81 | 1918.81 | 0.016547 | 19 | 4.16 | 2 | High | Low | 1023 | 348 | 0 | 0 | 0 | 5.91 | 0 | 3.95 | 63 | 76 | 0 | 0 | NR | 0% | [5 empty] | 100% |  |  |  | X | X | X | X | X | X | X | 2020 |  | Next WMP | Next WMP
Eagle | Pineknot | 2072.3467 | 2072.3467 | 0.017871 | 16 | 4.16 | 2 | Medium | Medium | 959 | 323 | 0 | 0 | 0 | 7.38 | 0 | 1.53 | 16 | 104 | 0 | 0 | NR | 0% | [5 empty] | 33.33% |  |  |  | X | X | X | X | X | X | X | 2020 |  | Next WMP | Next WMP
Harnish (Village) | Village | 385.44 | 385.44 | 0.0033239 | 21 | 4.16 | 2 | Medium | Low | 254 | 83 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 13 | 38 | 0 | 0 | NR | 0% | [5 empty] | NA |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Garstin | Meadow | 2439.81 | 2439.81 | 0.02104 | 15 | 4.16 | 2 | High | Low | 1055 | 277 | 0 | 0 | 0 | 5.91 | 0 | 3 | 15 | 124 | 0 | 0 | 7 | 0% | [5 empty] | 25% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Lagonita | Village | 2023.36 | 2023.36 | 0.017449 | 17 | 4.16 | 2 | Medium | Low | 1103 | 453 | 0 | 0 | 0 | 7.46 | 0 | 1.43 | 60 | 116 | 0 | 0 | 9 | 0% | [5 empty] | 100% |  | X |  | X | X | X | X | X | X | X | 2021 |  | Next WMP | Next WMP
Interlaken | Meadow | 3274.95 | 3274.95 | 0.028242 | 13 | 4.16 | 2 | High | Medium | 880 | 280 | 0 | 0 | 0 | 6.45 | 0 | 3.55 | 27 | 113 | 0 | 0 | 2 | 0% | [5 empty] | 50% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Castle Glen (Division) | Division | 1982.48 | 1982.48 | 0.017096 | 18 | 4.16 | 2 | Medium | Medium | 1188 | 343 | 9 | 0 | 0 | 6.93 | 0 | 3.68 | 45 | 80 | 0 | 0 | 10 | 0% | [5 empty] | 100% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Country Club | Division | 983.6467 | 983.6467 | 0.0084826 | 20 | 4.16 | 2 | Medium | High | 605 | 180 | 0 | 0 | 0 | 3.18 | 0 | 0.94 | 10 | 15 | 0 | 0 | NR | 0% | [5 empty] | 33.33% |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Fox Farm | Meadow | -8 | 0 | -6.8989e-05 | 26 | 4.16 | 2 | Low | Low | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2022 |  | Next WMP | Next WMP
Pump House (Lake) | Lake | 287.04 | 287.04 | 0.0024753 | 22 | 4.16 | 2 | High | High | 4 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 10 | 0 | 0 | NR | 0% | None |  |  |  |  | NA |  | X |  | X | X | X | X | X | X | X | 2020 |  | Next WMP | Next WMP
Lift (Summit TOU) | Summit | 27.6 | 27.6 | 0.00023801 | 23 | 4.16 | 2 | Low | Low | 1 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 0% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 |  | Next WMP | Next WMP
Skyline (Summit Res) | Summit | 0 | 0 | 0 | 24 | 4.16 | 2 | Low | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2023 | NA | NA | Next WMP
Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 0 | 24 | 4.16 | 2 | Low | Low | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR | 100% | None | NA |  | NA | NA | NA |  | X |  | X | X | X | X | X | X | X | 2022 | NA | NA | Next WMP
|  | 115960.9762 | 115968.9762 | 1 | [6 empty] | 9951 | 9 | 0 | 0 | 210.9 | 0 | 54.08 | 816 | 1872 | 0 | 0
|  | Wildfire Risk Groups | [20 empty] | Status
|  | High | [21 empty] | Not Started
|  | Moderate | [21 empty] | In Progress
|  | Low | [21 empty] | Complete or Implemented
Not Applicable
[15 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[15 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[14 empty] | 34 kV | 28.93 | 0 | 0.91 | 29.84
[14 empty] | 4 kV | 181.97 | 0 | 53.17 | 235.14
[14 empty] | Total | 210.9 | 0 | 54.08 | 264.98
[15 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[14 empty] | 34 kV | 10.92% | 0% | 0.3434% | 11.26%
[14 empty] | 4 kV | 68.67% | 0% | 20.07% | 88.74%
[14 empty] | Total | 79.59% | 0% | 20.41% | 100%
[15 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[14 empty] | 34 kV | 96.95% | 0% | 3.05%
[15 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[14 empty] | 4 kV | 77.39% | 0% | 22.61%

## List
Vegetation Density |  | Wind Intensity |  | Worst Circuit
High | 100 | High | 100 | 1 | 1000
Medium | 25 | Medium | 25 | 2 | 900
Low | 5 | Low | 5 | 3 | 800
|  |  |  | 4 | 700
|  |  |  | 5 | 600
|  |  |  | 6 | 500
|  |  |  | 7 | 400
|  |  |  | 8 | 300
|  |  |  | 9 | 200
|  |  |  | 10 | 100
|  |  |  | NR | 0

## Risk Scoring
Risk Factor | Risk Scoring Amount (Adds to Risk Score) | Risk Mitigation Factors | Risk Scoring Amount (Subtracks from Risk Score)
Available energy | 34.4 kV = 500 & 4 kV = 50 | Pole Loading Program (Percent Complete) | (Number of Wood Poles x Percent Complete) x 5; NA = 0
Fire Threat District | HFTD Tier 3 = 10000 x Bare Wire Circuit Miles and HFTD Tier 2 = 50 x Bare Wire Circuit Miles | FI Program (Percent Complete) | (Percent Complete * 100) x 2; NA = 0
Length of overhead bare wire | Bare Wire Circuit Mile x 200 | Enhanced Vegetation Management | On Schedule (Green) = Bare Wire Circuit Miles x 2; Behind Schedule (Red) = 0
Availability of fuel | High Density = 100 x Bare Wire Circuit Miles; Med Density = 25 x Bare Wire Circuit Miles; and Low Density = 5 x Bare Wire Circuit Miles | GO-165 Ground Patrol | In Periodicity (Green) = Bare Wire Circuit Miles x 2; Out Periodicity (Red) = 0
Susceptibility to high winds | High Wind Area = 100 x Bare Wire Circuit Miles; Med Wind Area = 25 x Bare Wire Circuit Miles; and Low Wind Area = 5 x Bare Wire Circuit Miles | GO-165 5-Year Inspections | In Periodicity (Green) = Bare Wire Circuit Miles x 2; Out Periodicity (Red) = 0
Number of conventional | # of Conventional Fuses x 2 | GO-165 Intrusive Inspections | In Periodicity (Green) = Number of x 2; Out Periodicity (Red) = 0
Number of Tree attachments | # of Tree Attachments x 4 | Bi-Annual LiDAR Survey | In Periodicity (Green) = Number of Wood Poles x 2; Out Periodicity (Red) = 0
Number of Uncorrected Level 1 deficiencies | # of Level 1 Deficiencies x 1000 | 3rd Party Annual Ground Patrol | In Periodicity (Green) = Bare Wire Circuit Miles x 2; Out Periodicity (Red) = 0
Number of Uncorrected Level 2 deficiencies | # of Level 2 Deficiencies x 100 | GO-174 Substation Inspections | In Periodicity (Green) = Bare Wire Circuit Miles x 2; Out Periodicity (Red) = 0
Rank in Top Ten worst performing circuits | #1 = 1000, #2 = 900, #3 = 800, #4 = 700, #5 = 600, #6 = 500, #7 = 400, #8 = 300, #9 = 200, #10 = 100, & Not Ranked = 0

## Circuit Fire Safety Measures
Circuit Fire Safety Measure | Required Action for Each Circuit in Order to Call Complete
Exacter Survey | Perform Exacter survey on circuit.
Pole Loading Program | Perform Pole Loading Progam on circuit. (Pole Loading Program includes the following: perform pole loading analysis, perform intrussive testing if not performed within 5 years, evaluate the pole for repair or replacement and take all necessary corrective action (repair or replacement).
Tree Attachment Removal Program | Remove all tree attachments from circuit.
Tree Wire | Evaluate if Tree Wire is warranted. If warranted; then plan, obtain funding, procure, and install.
Replace Expulsion Fuses | Evaluate if any expulsion fuses must be replaced with current limiting fuses. If replacements are warranted; then plan, procure, and replace them.
Fuse Trip Savers | Evaluate if any fuses should be replaced by fuse trip savers and evaluate if any fuse trip savers should be added in addition to existing fuses. If it is deemed that fuses should be replaced and/or fuse trip savers should be added; then plan, procure, and install fuse trip savers.
Fault Indicators | Evaluate if fault indicators (FIs) should be installed in the circuit. If it is deemed that FIs should be installed; then plan, procure, and install FIs.
Pulsing Auto Reclosers | Evaluate if pulsing auto reclosers (ARs) should be installed in the circuit. If it is deemed that pulsing ARs should be installed; then plan, procure, and install them.
IntelliRupters Pulse Closers Fault Interrupter | Evaluate if IntelliRupters Pulse Closers Fault Interrupters should be installed in the circuit. If it is deemed that IntelliRupters Pulse Closers Fault Interrupters should be installed; then, plan, procure, and install them.
System Instrumentation | Install circuit level metering (3 phase). Evaluate if further instrumentation is warranted. If it is deemed that further instrumentation is necessary; then plan, procure, and install the instrumentation.
Switch Automation Opportunities | Evaluate if switch automation opportunities exist that would enhance fire safety. If it is deemed that switch automation should be installed; then plan, procure and install device automation.
Branch Line Fusing options | Evaluate if branch line fusing opportunities exist that would enhance fire safety or if existing branch line fusing should be changed to enhance fire safety. If it is deemed that branch line fusing should be installed; then plan, procure and install branch line fusing.
Evaluate Protective Settings | Evaluate breakers, switches, reclosers, fuse trip savers, fuses and other trip devices. Document the devices and settings for each circuit and make setting adjustments as deemed necessary. Each circuit should have a listing of potective devices with settings.